## Sheet1
常 州 思 源 东 芝 变 压 器 有 限 公 司 Changzhou Sieyuan Toshiba Transformer C0.,Ltd
投标初评表
项目名称 |  | 测算单号
项目台数 |  | 营销经理
变压器设计寿命(年) |  | 是否并联运行？
变压器型号 |  | 质量保证年限
注意是否为新规（超高电压等级、超大容量、异常容量/电压比、超高阻抗等）产品，特殊点在重要说明事项中列出
1.运行环境
1.1 | 运行场所 | 1.6 | 海拔高度(m)
1.2 | 最高温度(℃) | 1.7 | 最低温度(℃)
1.3 | 年平均温度(℃) | 1.8 | 月平均温度(℃)
1.4 | 最大风速(m/s) | 1.9 | 最大日照强度(W/cm2)
1.5 | 污染程度 | 1.1 | 环境腐蚀等级
2.基本参数
2.1 | 执行标准
2.2 | 频率(Hz)
2.3 | 噪声水平(dB)声压级/声功率
2. 4 | 额定容量(MVA)
2.5 | 联结组别
2.6 | 开关类型
2.7 | 相数
2.8 | 冷却方式
2.1 | 额定电压(kV)
2.11 | 绝缘水平
2.13 | Highest Voltage for equipment winding 设备最高电压 Um(kV)
2.14 | Full Wave Lightning Impulse 雷电全波冲击电压 LI or BIL(kV)
2.15 | Chopped Wave Lightning Impluse 雷电截波冲击电压 LIC(kV)
2.16 | Switching impluse 操作冲击电压 SI(kV)
2.17 | line terminal ACwithstand 工频耐受电压 AC(kV)
2.18 | 系统短路电流(kA)
2.19 | 短路持续时间(s)
2.2 | 局部放电(pC)
2.21 | 阻抗电压(%)、X/R的值
2.22 | 空载损耗(kW)
2.23 | 负载损耗(kW)
2.24 | 效率(%)
2.25 | 顶层油温升(K)
2.26 | 绕组平均温升(K)
2.27 | 绕组热点温升(K)
2.28 | 铁心温升(K)
3.铁心部分
3.1 | 型式
3.3 | 磁通密度(T)
3.4 | 激磁电流(%)
3.5 | 铁心装配方面的要求
3.6 | 铁心绝缘耐热等级
3.7 | 谐波要求
4.线圈部分
4.1 | 电流密度(A/mm2)
4.2 | 绝缘纸类型
7.保护装置
部件名称
7.1 | 绕组温度计
7.2 | 油温计
7.3 | 气体继电器
7.4 | 油位计(OLTC)
油位计(本体)
7.5 | 突发压力继电器
7.6 | 呼吸器(本体)
呼吸器(OLTC)
7.7 | 压力释放阀
7.8 | 突发压力继电器
8.监测装置
8.1 | 光纤测温装置/直接测量温度/预估寿命
8.2 | 气体在线监测装置/油色谱
8.3 | 充氮灭火装置(是否需要防爆功能)
8.4 | 套管在线监测装置
8.5 | 局放监测装置
8.6 | 胶囊泄露监测
8.7 | 信号集中器
8.8 | 综合类在线监测
8.9 | 变压器在线监测系统
9.冷却设备
9.1 | 片散
9.2 | 涂漆(热镀锌)
9.3 | 片散中间片涂漆要求
9.4 | 冷却装置挂本体/分体
9.5 | 风扇
9.6 | 油泵
9.7 | 冷却器
10.运输及尺寸限制
10.1 | 运输方式
10.2 | 变压器运输类型
10.3 | 冲撞记录仪要求及是否带GPS
10.4.1 | 运输尺寸及重量限制要求
10.4.2 | 安装尺寸及重量限制要求
11.绝缘油类型
11.1 | 油类型
11.2 | 油厂家
11.3 | 备用油
11.4 | 油运输方式
12.油箱
12.1 | 油箱压力强度
12.2 | 油箱真空强度
12.3 | 防腐设计分类/涂层规格
12.4 | 箱盖固定方式
12.5 | 焊缝测试
12.6 | 紧固件
12.7 | 密封件
12.8 | 小车
12.9 | 减震垫
12.1 | 是否油箱防爆要求
12.11 | 电缆罩
12.12 | 本体储油柜
12.13 | 开关储油柜
13.油补偿系统
13.1 | 型式
13.2 | 主油箱吸湿器型式要求
14.端子箱及控制柜
14.1 | 外壳材质
14.2 | 辅助电源要求
14.3 | 是否带漏电保护
14.4 | 二次电缆
14.5 | 端子要求
15.招标文件要求的其它非标附件
15.1 | 中性点接地装置要求
15.2 | 中性点接地电阻要求
15.3 | 铁心接地电流监测要求
15.4 | 智能组件柜要求
15.5 | 防跌落系统要求
15.6 | 热虹吸过滤器要求
15.7 | 火灾探测器要求
16.备品备件
16.1 | 备品备件要求
17.试验
17.1 | 试验要求
18.电流互感器
18.1 | 电流互感器要求
Note on L6: 1 unit
Note on AD7: Transformer to be operated in parallel with the other transformers (Yes, No) Yes
Note on L15: Temperature of cooling air, not to exceed 40oC
Note on L16: Average temperature of the cooling air for any 24 h period, not to exceed 30oC
Note on U22: ANSI/IEEE C.57.12.90
Note on U23: Frequency, Hz 60
Note on U24: Average audio sound pressure level not more than,dB ≤ 100
Note on L25: The maximum continuous loading in the respective windings without exceeding the temperature rise limitations under each cooling conditions at rated voltage and frequency shall be as follows: H-winding 100, X-winding 100, Y-winding 30
Note on L26: Angular displacement for three-phase transformers (specify ANSI Std. or vector group symbol if IEC Std.is applied) Yna0d1
Note on L27: An On-load tap changing mechanism shall be furnished and provided for the transformer: Yes
Note on L28: High Voltage Winding, kV 230kV (±10%) at 1% tap step
Note on U29: Type of cooling ONAN/ONAF/ONAF
Note on AD29: Self-cooled rating (ONAN), MVA 60, 1st stage cooling rating, MVA 80, 2nd stage cooling rating, MVA 100
Note on I30: Nominal system voltage (kV rms): H-winding, kV 230, X-winding, kV 69, Y-winding, kV 13.8
Note on I31: Short-duration power frequency withstand voltage (kV rms): H-winding, kV 460, X-winding, kV 140, Y-winding, kV 38
Note on I32: Maximum system voltage (kV rms): H-winding, kV 245, X-winding, kV 72.5, Y-winding, kV 17.5
Note on I33: Lightning Impulse Withstand Voltage (kV crest): H-winding, kV 1050, X-winding, kV 350, Y-winding, kV 95
Note on I35: Switching Impulse Level (kV crest): H-winding, kV Not required
Note on I38: Required number of hours for overload with top oil MVA 4hrs
Note on I39: On-line Partial Discharge Monitoring System
Note on L40: % Impedance at rated voltage and frequency and based on maximum MVA rating and 85oC1 H-X winding2 12.51%
Note on L41: No-load loss, kW (NL-L) 40
Note on L43: Load Losses, kW (LL),at 850C ONAN rating 257
Note on L46: Temperature Rise, oC (at rated power) Top Oil ≤ 65
Note on L47: Temperature Rise, oC (at rated power) Winding ≤ 65
Note on L53: Core construction (Core, shell) core
Note on L55: Exciting current at rated voltage and frequency and based on maximum MVA rating of high voltage winding,not more than 1.5%
Note on U72: Supply of dial-type temperature indicators mounted on the transformer for top oil and hot spot winding temperatures mounted side by side with each other inside the local control cabinet which are visible from the outside without opening the cabinet door Yes
Note on U73: Supply of dial-type temperature indicators mounted on the transformer for top oil and hot spot winding temperatures mounted side by side with each other inside the local control cabinet which are visible from the outside without opening the cabinet door Yes
Note on U74: A single-float Buchholz relay shall be provided for each main conservator connected to the highest point of the conservator as leakage detector for the diaphragm of the air-bag type: (Yes, No) Yes
Note on U77: Sudden pressure relay, required (Yes, No) Yes
Note on U78: Maintenance Free Dehydrating (silica gel) Breathers for the Transformers
Note on U80: Pressure relief device of each type used 1 each
Note on U81: Sudden pressure relay, required (Yes, No) Yes
Note on L86: Supply of intelligent on-line continuous gas-in-oil incipient fault detection system for nine (9) key gases namely: hydrogen, methane, carbon monoxide, carbon dioxide, ethylene, ethane, acetylene, nitrogen, and oxygen
Note on L88: On-Line Diagnostics for Transformer Bushings
Note on L89: On-line Partial Discharge Monitoring System
Note on L92: Transformer monitoring equipment shall be inclusive of: Installation of transformer on-line monitoring devices including tools/materials to be used
Note on L93: Transformer monitoring equipment shall be inclusive of: Installation of transformer on-line monitoring devices including tools/materials to be used
Note on U97: Coolers (specify radiator,cooler tubes) Radiator fin type
Note on U101: Fan motor supply voltage, V 230V, 3-phase, 60Hz
Note on U115: Insulating oil shall be mineral oil in accordance with ASTM D3487 (Type I, Type II) Type II
Note on U117: Insulating oil in sealed non-returnable drums (this is in addition to the 5% excess mentioned in Paragraph 3.2.2.12.6 of the technical specification). of each type used 500 liters
Note on U129: Standard Skid Base of Heavy Steel (with or without wheels) With wheels
Note on U133: The conservator type of oil preservation system of the transformer shall be of the: (specify diaphragm, nitrogen gas sealed, etc.) Diaphragm
Note on J144: The items listed below shall be designed to receive the following auxiliary voltage source.
Note on U163: Bushings for the high voltage terminals complete w/ gaskets and oil, if oil-filled: “H” terminals 1 unit
Note on U167: Routine Tests to be performed on all the transformers Yes
Note on U171: Bushing current transformers shall be supplied at the following terminals: H, X, Y and Neutral